**SAMPLE SPECIFICATION**

**MODEL REH & RXH**

**SPLIT SYSTEM**

**General Section**

Provide packaged, Outdoor heating (and cooling) units with separated combustion as Reznor® brand equipment.

The units shall be (the REH series utilizing electric heating elements) (RXH air handling unit) designed for rooftop or outdoor slab. The unit shall be specifically design for make-up air and space control applications, meeting all the requirements found in AHSRAE standard 90.1 and 62.2. The unit shall be modular such DX cooling, DX cooling with reheat, chilled water cooling, evaporative cooling, hotwater heat, and mixing box sections can be added to the unit configuration.

**Power**

All units shall be equipped for use with (115/1) (208/1) (230/1) (208/3) (230/3) (460/3) (575/3) unit supply voltage. The unit shall have single power connection for 3 phase or 1 phase wiring with factory installed distribution blocks. The unit shall have (unit mounted, non-fusible, nema 4X, lockable disconnect switch) (factory supplied, field installed, non-fusible, lockable, nema 1) field mounted disconnect switch) (factory supplied, field installed, fusible, lockable, nema 1 disconnect switch). The control voltage wiring shall be class 2, 120Vac and/or 24Vac/dc. Unit shall have (over/under voltage or phase loss protection); (factory supplied, field powered convenience outlet ground-fault circuit interrupter).

**Blower & Air Control Section**

The base unit blower shall include an adjustable belt-driven centrifugal fan with (open dripproof) (totally enclosed) (premium efficiency) motor. The motor shall have [rubber][spring] vibration isolated with (contactor) (motor starter) (variable frequency drive). Fan shall have air proving switch inter-locked with gas controls to prevent gas heat operation when the fan is not operational. The blower shall use (solid-belt) (linked belt). The blower assemble shall be factory set to specified CFM at the given static pressure. The blower assembly shall have adjustable sheave for airflow adjustment. (The blower assembly shall be shipped with spare belts). Unit shall have [1” or 2” disposable] [1” or 2” permanent] [2” MERV 8] [4” MERV 13 pleated] filters.

**Electric Heat Section**

(Unit shall include blow through electric resistance heating section using open element with insulated ceramic bushing, fuses, contactors, auto reset high temperature limit switch and other necessary safety devices. Provide capacity sizes and staged/modulating control as shown on the schedule. The furnace shall be equipped with all required safety elements. Unit shall have a (one-stage heat control for recalculating air space temperature control) (2-stage heat control for recalculating air space temperature control) (2-stage heating/3-stage cooling digital controller for MUA applications with space temperature reset) (SCR electronic modulation heating /3-stage cooling digital for MUA applications with space temperature reset).)

**Hot Water Heat Section**

(Unit shall have custom configured hot water coil to maximize thermal efficiency and system performance with the given GPM and fluid temperatures. The coil shall be design for ( x% Ethylene) (X % Proplylene) (No) glycol. (The coil shall have turbospiral tubes for fluids with glycol percentages above 20%.) The coils shall have (left) (right) hand connections. Coil casing shall have (galvanized) (stainless steel) material construction. The custom hot water coil shall have quarter, half, ¾ or full circuiting to meet the schedule performance. The coil shall have 1 - 4 rows, 8 – 14 fins per inch, fluid pressure drop less than 18 psi to meet the scheduled performance. Manufacture shall provide detail coil performance sheet. ½” or 3/8” tube size to meet the given schedule coil performance. (Coil shall have electro-fin polymeric coating for sea coast and other corrosive environment applications.) Hot water control valve shall be provided by temperature controls contractor.)

**Cooling Section**

Unit shall have draw thru cooling coil section that can provide condition of air per the schedule. The coil module shall be configurable to handle DX or chilled water coil. The coil module shall have double wall construction with insulation value of (R-3.8) (R 4.4). Coil cabinet shall have sloped slide out stainless steel drain pan under all coils per ASHRAE std 62.1. The airflow shall be limited to 500 FPM to prevent water blow off from the coil. (Cooling coil cabinet to include UVC lamp for neutralization of VOCs and microorganisms for improved IAQ).

(Unit shall have custom configured DX evaporate coil to maximize thermal efficiency and system performance with the selected condenser unit. The coil shall be (single circuit) (two stage 50%-50% dual interlaced) (3 stage 33%-66% interlaced) (2 Stage unequal 40% -60% interlaced). The coils shall have (left) (right) hand connections. Coil casing shall have (galvanized) (stainless steel) material construction. The custom coil shall have 3 to 6 rows, 8 – 14 fins per inch, 200 to 500 FPM air flow, and ½” or 3/8” tube size to meet the given schedule coil performance. (Coil shall have electro-fin polymeric coating for sea coast and other corrosive environment applications.) (Unit shall be supplied with thermal expansion valve for each circuit.) (Unit shall be equipped with unit mounted reheat. Reheat system shall be self contained requiring no external piping connections. The reheat shall provide useful primary cooling of entering air meeting ASHRAE std 90.1 efficiency guidelines. The reheat coil position shall include a minimum separation of 4” from the cooling coil to eliminate re-evaporation of cooling coil condensate. Modulating capacity control not required unless necessary to maintain proper discharge air control.))

(Unit shall have custom configured chilled water evaporate coil to maximize thermal efficiency and system performance with the given GPM and fluid temperatures. The coil shall be design for ( x% Ethylene) (X % Proplylene) (No) glycol. (The coil shall have turbospiral tubes for fluids with glycol percentages above 20%.) The coils shall have (left) (right) hand connections. Coil casing shall have (galvanized) (stainless steel) material construction. The custom chilled water evaporator coil shall have quarter, half, ¾ or full circuiting to meet the schedule performance. The evaporator coil shall have 4 or 6 rows, 8 – 14 fins per inch, 200 to 500 FPM air flow, and fluid pressure drop less than 18 psi to meet the scheduled performance. Manufacture shall provide detail coil performance sheet. ½” or 3/8” tube size to meet the given schedule coil performance. (Coil shall have electro-fin polymeric coating for sea coast and other corrosive environment applications.))

**Evaporative Cooling Section**

(Provide evaporative cooling module as manufactured as Reznor® brand for makeup air application. Cabinet shall constructed of weatherized (aluminized steel) (stainless steel) for outdoor installation. A mesh screen will cover the air intake opening. Unit shall be provided with height adjustable legs. Units shall be equipped with terminal block wiring for use with 115 (208, 230) volt supply voltage. Cabinet bottom shall have overflow and drain connections and a 300 series grade stainless steel water reservoir. Module shall be equipped with pump and float control system including electrical motor with stainless steel arm, thermally protected water pump, float switch and bleed line connections (Aqua Saver® water metering system with solenoid valve and timer). Evaporative cooling media supplied to be 12 inches in size and to be made of (rigid cellulose material, rigid glass fiber material-UL rated). Equipment shall include (moisture elimination pad) and (drain and fill kit) and (water hammer arrestor).)

**CONTROLS Section**

Unit shall be equipped with factory installed contactors, relays, sensor, switches to perform (analog discharge air control) (DDC make-up air with space temperature reset control. The unit shall control blower, heating, cooling & reheat functions.) (External BMS interface control) (Space thermostat control). The unit shall have label terminal blocks and unit mounted ladder logic wiring diagram.

**Cabinet Section**

Packaged unit may have factory-attached modules:- (mixing box for inlet air with selection of outside and return entering air configurations [top, bottom, rear combinations with or without screens], outside or outside and return air dampers modulating economizer controls with direct-coupled 24VAC spring return actuators. Construction of mixing box will be double wall, [insulated] [high density insulated]). The (double wall [insulated] [high density insulated]) blower section shall be supplied with (horizontal supply opening) (horizontal supply air inlet opening with duct flanges) (Horizontal supply with downturn plenum) (screened horizontal supply air inlet opening with duct flanges). (The unit shall have outside air hood with permanent filters designed for 100% unit air flow from outside with zero water/snow entrainment. The hood shall meet ASHRAE std 62.1 entrainment intent.)

The packaged system shall have a pre-coat RAL 1001 white paint finish. Finish shall be a minimum 80 gloss on G30 galvanized steel. Cabinet shall be arranged for [slab mounting] [roof mounting with curb]. Control, burner, and blower service compartment doors shall be hinged. Blower door hardware shall be heavy duty stainless. Control and burner door hardware shall have heavy duty external hardware. (Cabinet shall have through-the-base electrical supply knockout.)

**OPTIONAL ACCESSORIES**

The following features will be factory installed: (duct flanges); (discharge louvers [horizontal] [horizontal and vertical]); (firestat); (discharge temperature low limit), (high, low, or high and low gas pressure switches); and (relays). The following accessories will be provided: horizontal or vertical vent/combustion air kit; (downturn nozzle [25- 65° with or without vertical louvers] [50-90° with or without vertical louvers]); (gas pressure regulator); and (remote console)

**CERTIFICATION**

The packaged heating and cooling system shall be design-certified to ANSI Z83.8 and CSA 2.6 Standards. The energy usage shall be designed to meet ASHRAE Standard 90.1. See specific information for sizes and capacities. Product manufacturer must have minimum of 40 years of experience with separated combustion heating equipment. Product to be warranted to the original owner/user to be free from defects in material or workmanship. Limited warranty to be for twelve (12) months from date of installation or eighteen (18) months from date of shipment from manufacturer, whichever occurs first.